## Slide 1: 800V DC in Data Centers
Henrik Nilén

## Slide 2: AI - A Paradigm Shift for Data Centers
Compute rack power

## Slide 3: DC Power in the Data Center - Background
DC in the data center started 15 years ago
Driven by hyperscalers and the Open Compute Project
DC power and batteries in each rack gain efficiency and power density
AI servers now drive
Higher power per rack
Increase cables and voltage drop
The answer is 800VDC
IT

## Slide 4
400Vac
Power shelf
50Vdc
AC UPS
30-250kW/rack (1P PSU)
120-300kW/rack (3P PSU)
10/13.8/20/34.5kVac
400Vac
Chip
Power shelf
50Vdc
400Vac
Chip
0.xV
Power shelf
50Vdc
HVDC (sidecar or centralized)
+/-400Vdc
or
800Vdc
Chip
Chip
800Vdc
Chip
MVDC
MVDC Power Center
BESS
Renewables & Fuel Cells
MV/LV
30-140kW/rack
250-600kW/rack
250kW～1MW/rack
Busbar
Busbar
Busbar
Busbar
Busbar
Improve efficiency
Optimize architecture
No space for BBU&PSU
Rack busbar challenge
Input cable challenge
Rack busbar challenge
Optimize architecture
Improve efficiency
Optimize architecture
Multi energy integration
Micro-grid
Grid
Battery Backup
12V
0.xV
12V
0.xV
12V
0.xV
0.xV
HVDC Server
HVDC Server
50Vdc
50Vdc
AI Datacenter Power Train Evolution
Server Rack
Power
Server Shelf
Source: Vertiv 2025

## Slide 5: Vertiv Higher Voltage DC Power Footprint
First 240VDC system in the industry was deployed.
The first 400VDC system in the industry deployed in France Telecom.
1st 240V HVDC system in China was launched.
1st generation 400V HVDC system was launched.
2nd generation 240/400V DC system were launched.
3rd 240/400V 25kW rectifier system released.
In August 2019, the prefabricated solution APT-2.0 DC system was launched.
APT-2.0 DCS system using phase-shifting transformer.
4th generation 240/400V DC system.
5th generation
+/-400VDC
800VDC
system
2008 2010 2012 2014 2018 2023 2024 2025

## Slide 6: Mt Diablo – An Open Compute +/-400VDC Power Solution
Powering high density AI racks
Leveraging electric vehicle tech
Developed by Microsoft, Meta and Google
Disaggregated sidecar design
Up to 1MW per rack
Includes power, BBU, CBU and distribution
Open source specification

## Slide 7: Why CSPs adopt +/-400VDC?

## Slide 8: +/- 400VDC Solution
BBU+CBU
PSU
AC & DC
PDU
+400VDC
-400VDC
0
AC Input
400/50
DCDC
50VC server
Server Rack
Server Rack
400/50
DCDC
50VDC server
Server Rack
800VDC
Busbar
Server Rack
800/50
DCDC
50VDC server
DC Output
800VDC server

## Slide 9: NVIDIA 800VDC Architecture
54V DC Limits: Space constraints, Copper overload, Inefficient conversion steps
800V DC benefits: Scalability, Efficiency, Copper reduction, Reliability, Future-proofing
Key numbers: 800VDC  5% efficiency gain, 70% maintenance cost reduction

## Slide 10: Conclusions
AI servers demand lots of power. 1MW per compute racks in a few years
Space constraints, copper overload and voltage drop drive towards higher voltage power systems
Disaggregated power is a trend. First sidecar in white space, later in grey space
Native 800VDC servers will help reduce power losses
The future will bring even higher voltage solutions

## Slide 12
12
High Resistance Midpoint Grounding Concept
High Resistance Mid-Point Grounding (HRMG, GFD required)
High resistance midpoint grounding (HRMG) makes 800V DC safe with regard to electrical shock (line to ground type) with the limitation of human body current for line to ground (7.5mA for 110kOhm each resistor, IEC Zone II)
No arc flash to ground during single ground fault utilizing HRMG
Ground fault detect (GFD)
Ground fault detect(GFD) module equipped with an insulation resistance measuring circuit to check the resistance between 800V, Rtn and PE.
GFD module also applies switching resistor topology to calculate the symmetrical ground fault.
800V DC
Rtn
800V DC
Rtn
800V
+400V
-400V
Hi-resistance mid-point grounding scheme

## Slide 13: Health and Safety
I - Normally no perception
II - No dangerous physiological
effect, risk of startle reaction
III - Risk of muscular reaction
IV - Critical effects, risk of
ventricular fibrillation
Average human body resistance =1500 ohm (200-400V)
230/277VAC - IV
120VAC - III
400VDC (one pole) – III
400VDC direct midpoint - III
400VDC
midpoint 50kΩ - II
48VDC - II
RCD 30mA/200ms
RCD –residual current device (in US and Canada also known as GFI or GFCI)
800VDC direct midpoint – III
800VDC
midpoint 50kΩ - II
800VDC (one pole) – IV